## Label
SHELL-AND-TUBE HEAT EXCHANGER DESIGN
Vc | cold fluid volumetric flow rate | Vh | hot fluid volumetric flow rate | Rdtube | fouling factor for tube | Rdshell | fouling factor for shell
mc | cold fluid mass flow rate | mh | hot fluid mass flow rate | Dtube_i | internal tube diameter | Dshell | shell diameter
|  |  |  | Dtube_e | external tube diameter | Rd | average fouling factor
Tc1 | cold temperature in | Th1 | hot temperature in | nt | number of tubes | np | number of passes
Tc2 | cold temperature out | Th2 | hot temperature out | Lt | tube length | P | Pitch spacing
Tcm | average cold temperature | Thm | average hot temperature | at | tube cross-sectional area | B | Baffle spacing
dTc | cold temperature difference | dTh | hot temperature difference
[5 empty] | Inner Fluid Properties |  | Outer Fluid Properties
Cpc | cold fluid specific heat | Cph | hot fluid specific heat | ai | cross-sectional area | ao | cross-sectional area
kc | cold fluid thermal capacity | kh | hot fluid thermal capacity | mi | mass flow rate | mo | mass flow rate
uc | cold fluid dynamic viscosity | uh | hot fluid dynamic viscosity | Cpi | specific heat | Cpo | specific heat
ro_c | cold fluid specific mass | ro_h | hot fluid specific mass | ki | thermal capacity | ko | thermal capacity
|  |  |  | ui | dynamic viscosity | uo | dynamic viscosity
|  |  |  | ro_i | specific mass | ro_o | specific mass
dTlm | log mean temperature difference |  |  | Gi | mass flux | Go | mass flux
Q | exchanged heat |  |  | Re_i | Reynolds number | Re_o | Reynolds number
R | R factor |  |  | Pr_i | Prandtl number | Pr_o | Prandtl number
S | S factor |  |  | vi | velocity | vo | velocity
F | correcting F factor |  |  | hi | convection heat transfer coefficient | ho | convection heat transfer coefficient
dT | true temperature difference |  |  | hii | convection heat transfer coefficient (fix) | Tw | wall temperature
|  |  |  | u'i | corrected dynamic viscosity | u'o | corrected dynamic viscosity
|  |  |  | phi_i | dynamic viscosity ratio | phi_o | dynamic viscosity ratio
|  |  |  | h'i | true convection heat transfer coefficient | h'o | true convection heat transfer coefficient

## Main
Flowrate (cold) |  |  | Flowrate (hot) |  |  | Pitch type |  |  | Inner |  |  | Outer
Vc | 1000 | ft³/hr | Vh | 500 | ft³/hr | Triangular | 1 |  | Rdtube | 0.001 | hr.ft².°F/BTU | Rdshell | 0.002 | hr.ft².°F/BTU | Rd | 0.003 | hr.ft².°F/BTU
mc | 50000 | lb/hr | mh | 30000 | lb/hr | Squared | 0 |  | Dtube_i | 0.049 | ft | Dshell | 1.771 | ft | Deq | 0.060646 | ft
[9 empty] | Dtube_e | 0.062 | ft |  |  |  | ral | 0.5 | ft
Temperatures (cold) |  |  | Temperatures (hot) | [5 empty] | nt | 302 | tubes | np | 2 | passes
Tc1 | 80 | °F | Th1 | 150 | °F |  |  |  | Lt | 16 | ft | P | 0.083333 | ft
Tc2 | 110 | °F | Th2 | 100 | °F |  |  |  | at | 0.0018857 | ft² | B | 0.41667 | ft
Tcm | 95 | °F | Thm | 125 | °F
dTc | 20 | °F | dTh | 40 | °F | dTlm | 28.8539 | °F | ai | 0.28475 | ft² | ao | 0.18891 | ft² | Uclean | 53.6342 | BTU/hr.ft².°F
[9 empty] | mi | 50000 | lb/hr | mo | 30000 | lb/hr | Udirty | 46.2004 | BTU/hr.ft².°F
Parameters (cold) |  |  | Parameters (hot) |  |  | Q | 1500000 | BTU/hr | Cpi | 1 | BTU/lb.°F | Cpo | 1 | BTU/lb.°F
Cpc | 1 | BTU/lb.°F | Cph | 1 | BTU/lb.°F | R. | 1.6667 |  | ki | 1 | BTU/hr.ft².°F | ko | 1 | BTU/hr.ft².°F | Area | 2416 | ft²
kc | 1 | BTU/hr.ft².°F | kh | 1 | BTU/hr.ft².°F | S. | 0.42857 |  | ui | 0.5 | cP | uo | 0.5 | cP | U | 45.2344 | BTU/hr.ft².°F
uc | 0.5 | cP | uh | 0.5 | cP | F | 0.47569 |  | ro_i | 50 | lb/ft³ | ro_o | 60 | lb/ft³ | Rd_true | 0.0034622 | hr.ft².°F/BTU
ro_c | 50 | lb/ft³ | ro_h | 60 | lb/ft³ | dT | 13.7254 | °F
[9 empty] | Gi | 175594.5432 | lb/ft².hr | Go | 158808.5827 | lb/ft².hr
[9 empty] | Re_i | 7113.5332 |  | Re_o | 7962.6279
[9 empty] | Pr_i | 0.5 |  | Pr_o | 0.5
[9 empty] | vi | 3511.8909 | ft/h | vo | 2646.8097 | ft/h
[9 empty] | hi | 110.837 | BTU/hr.ft².°F | ho | 138.3337 | BTU/hr.ft².°F
[9 empty] | hii | 87.597 | BTU/hr.ft².°F | Tw | 113.3685 | °F
[9 empty] | u'i | 0.5 | cP | u'o | 0.5 | cP
[9 empty] | phi_i | 1 |  | phi_o | 1
[9 empty] | h'i | 87.597 | BTU/hr.ft².°F | h'o | 138.3337 | BTU/hr.ft².°F

## Credits
ChemEng Brasil
Autor: | Lucas Joshua Pires
Ano: | 2017